November 2022

Annex 1 to guide for

connection of power-generating plants to the medium and high-voltage grid (>1 kV)

Type B

Version 1.2

Version log

|  |  |  |
| --- | --- | --- |
| **Version** | **Change** | **Date** |
| 1.0 | A translated version of the Danish Guide for Power generating plants MV and HV | 30-04-2018 |
| 1.1 | Update of annex | 29-10-2021 |
| 1.2 | Layout update. | 18-11-2022 |

Indholdsfortegnelse

[Version log 2](#_Toc142638579)

[Indholdsfortegnelse 3](#_Toc142638580)

[Annex 1. DOCUMENTATION FOR TYPE B POWER-GENERATING PLANTS 4](#_Toc142638581)

[B1.1. Documentation for type B power-generating plants (part 1) 4](#_Toc142638582)

[B1.2. Documentation for type B power-generating plants (part 2) 15](#_Toc142638583)

DOCUMENTATION FOR TYPE B POWER-GENERATING PLANTS

* 1. Documentation for type B power-generating plants (part 1)

Please complete the documentation with power-generating plant data before commissioning and send it to the DSO

* + 1. Identification

|  |  |
| --- | --- |
| Power-generating plant name:  |  |
| Global Service Relation Number (GSRN number):  |  |
| Plant owner name and address:  |  |
| Plant owner telephone number:  |  |
| Plant owner email address:  |  |

* + 1. Description of the power-generating plant

|  |  |
| --- | --- |
| Type: | Synchronous power-generating plant [ ] Power park module [ ]  |
| Primary energy source:\*Describe type: | Wind [ ] Solar [ ] Fuel [ ] Other\* [ ]  |
| Energy conversion technology: | Steam turbine [ ] Gas turbine [ ] Combined cycle plant[ ] Internal combustion engine [ ] Inverter-based [ ]  |
| Fuel type, if applicable:  |  |
| Manufacturer/model:  |  |
| Voltage at the POC (Uc):  |  |
| Nominal power (Pn):  |  |
| Minimum power (*Pmin*):  |  |
| Rated mechanical shaft power for drive system (*Pmech*) (only synchronous power-generating plants): |  |
| Is a process diagram available for the plant? (only synchronous power-generating plants)Document reference:  | Yes [ ] No [ ]  |
| Is a single-line diagram available showing settlement metering, online metering, ownership boundaries and operation manager boundaries? Document reference:  | Yes [ ] No [ ]  |

* + - 1. Generator information

Please only complete this section for **synchronous power-generating** plants.

|  |  |
| --- | --- |
| Manufacturer:  |  |
| Type/Model:  |  |
| Does the generator comply with relevant sections of the following European standards?: * DS/EN 60034-1, ‘Rotating electrical machines – Part 1: Rating and performance’, 2004
* DS/EN 60034-3 ‘Rotating electrical machines – Part 3: Specific requirements for turbine-type synchronous machines’, 1995
 | Yes [ ] No [ ]  |
| Is detailed generator documentation enclosed?If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Generator data

Please only complete this section for **synchronous** power-generating plants.

|  |  |  |  |
| --- | --- | --- | --- |
| **Description** | **Symbol** | **Unit** | **Value** |
| Rated apparent power : | Sn | MVA |  |
| Rated voltage: | Un | kV |  |
| Rated frequency: | fn | Hz |  |
| Rated Power Factor(cosφ): | cosφn | - |  |
| Rated minimum reactive power generation from PQ diagram: | Qmin,n | Mvar |  |
| Rated maximum reactive power generation from PQ diagram: | Qmax,n | Mvar |  |
| Synchronous speed: | nn | Rpm |  |
| Total moment of inertia for rotating mass (generator, drive system, etc.): | Jtot | kg⋅m2 |  |
| Total moment of inertia for generator: | JG | kg⋅m2 |  |
| Total moment of inertia for drive system: | JD | kg⋅m2 |  |
| Rotor type: | - | - | Salient poles [ ]  Distinct poles [ ]  |
| Stator resistance per phase: | Ra | p.u. |  |
| Temperature for resistance: | TR | ºC |  |
| Stator dispersion reactance per phase: | Xad | p.u. |  |
| Positive-sequence reactance, d axis: | Xd | p.u. |  |
| Transient reactance, d axis: | X’d | p.u. |  |
| Subtransient reactance, d axis: | X’’d | p.u. |  |
| Saturated positive-sequence reactance, d axis: | Xd,sat | p.u. |  |
| Saturated subtransient positive-sequence reactance, d axis: | X”d,sat | p.u. |  |
| Positive-sequence reactance, q axis: | Xq | p.u. |  |
| Transient reactance, q axis: | X’q | p.u. |  |
| Subtransient reactance, q axis: | X’’q | p.u. |  |
| Transient open circuit time constant, d axis: | T’d0 | s |  |
| Subtransient open circuit time constant, d axis: | T’d0 | s |  |
| Transient open circuit time constant, q axis: | T’q0 | s |  |
| Subtransient open circuit time constant, q axis: | T’’q0 | s |  |
| Potier reactance: | Xp | p.u. |  |
| Saturation point at 1.0 p.u. voltage: | SG1.0 | p.u. |  |
| Saturation point at 1.2 p.u. voltage: | SG1.2 | p.u. |  |
| Reactance, inverse-component: | X2 | p.u. |  |
| Resistance, inverse-component: | R2 | p.u. |  |
| Reactance, zero-component: | X0 | p.u. |  |
| Resistance, zero-component: | R0 | p.u. |  |
| Is the generator star point earthed? | - | - | Yes [ ]   No [ ]  |
| If yes, ground reactance: | Xe | Ohm |  |
| If yes, ground resistance: | Re | Ohm |  |
| Generator's short-circuit ratio(Rated): | Kc | p.u. |  |

* + - 1. Excitation system

Please only complete this section for **synchronous power-generating** plants.

|  |  |
| --- | --- |
| Manufacturer: |  |
| Type/Model: |  |
| Does the excitation system comply with relevant parts of the following European standards?: * DS/EN 60034-16-1:2011 ‘Rotating electrical machines – Part 16: Excitation systems for synchronous machines – Chapter 1: Definitions’
* DS/CLC/TR 60034-16-3:2004 ‘Rotating electrical machines – Part 16: Excitation systems for synchronous machines – Section 3: Dynamic performance’.
 | Yes [ ] No [ ]  |
| Is the power-generating plant equipped with excitation system as specified in section 4.4.5?  | Yes [ ] No [ ]  |
| Is detailed excitation system documentation enclosed?If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Generator or plant transformer

|  |  |
| --- | --- |
| Is the plant connected through a generator or plant transformer? If yes, fill in the remaining fields: | Yes [ ] No [ ]  |
| Manufacturer:  |  |
| Type/Model: |  |
| Is detailed transformer documentation enclosed? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + 1. Tolerance of frequency and voltage deviations
			1. Phase jump

|  |  |
| --- | --- |
| Does the power-generating plant remain connected during voltage phase jumps of 20 degrees at the POC as specified in section 4.1.1? If yes, please provide reference to documentation: | Yes [ ] No [ ]  |

* + - 1. Operating area for voltage and frequency

|  |  |
| --- | --- |
| Is the power-generating plant capable of remain connected to the public electricity supply grid within the voltage and frequency range specified in section 4.1.1 and 4.1.2 and on figure 4.1 and generating continuously within the normal operating range.If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Frequency change

|  |  |
| --- | --- |
| Will the power-generating plant remain connected in case of frequency changes of 2.0 Hz/s at the POC? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Permitted reduction of active power during underfrequency

|  |  |
| --- | --- |
| Is the active power reduction at underfrequency less than the limit specified in section 4.1.2.2?If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + 1. Tolerance of voltage deviations

|  |  |
| --- | --- |
| Does the power-generating plant stay connected to the public electricity supply grid during voltage dips as specified in section 4.1.3.3? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |
| Does the power-generating plant stay connected to the public electricity supply grid during voltage swells as specified in section 4.1.3.2? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Fast fault current

Please only complete this section for **power park modules**.

|  |  |
| --- | --- |
| Does the power park module supply fast fault current as specified in section 4.1.3.3 (b)? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + 1. Start-up and reconnection of a power-generating plant

|  |  |
| --- | --- |
| Is connection and synchronisation performed as specified in section 4.2?If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |
| Is it possible to bypass automatic synchronisation?If no, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + 1. Active power control
			1. Power response to overfrequency

|  |  |
| --- | --- |
| Is the power-generating plant equipped with a frequency response function for overfrequency as specified in section 4.3.1? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Absolute power limit function

|  |  |
| --- | --- |
| Is the power-generating plant equipped with an absolute power limit function as specified in section 4.3.2.1? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Ramp rate limit

|  |  |
| --- | --- |
| Is the power-generating plant equipped with ramp rate limit as specified in section 4.3.2.2? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + 1. Reactive power control
			1. Operating range

|  |  |
| --- | --- |
| Is the power-generating plant capable of supplying reactive power at Pn and varying operating voltages as specified in section 4.4.1? Where can documentation showing that this requirement has been met be found?  | Yes [ ] No [ ]  |
| Is the power-generating plant capable of supplying reactive power when active power varies as specified in section 4.4.1? Where can documentation showing that this requirement has been met be found?  | Yes [ ] No [ ]  |

* + - 1. Power Factor control

|  |  |
| --- | --- |
| Is the power-generating plant equipped with a Power Factor control function as specified in section 4.4.2? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Automatic Power Factor control

|  |  |
| --- | --- |
| Is the power-generating plant equipped with an automatic Power Factor control function as specified in section 4.4.3? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Q control

|  |  |
| --- | --- |
| Is the power-generating plant equipped with Q control function as specified in section 4.4.4? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + 1. Power quality

|  |  |
| --- | --- |
| Are the values in the provided documentation computed values?  | Yes [ ] No [ ]   |
| Are the values in the provided documentation measured values?  | Yes [ ] No [ ]  |
| Is a report documenting that the calculations or measurements comply with the emission requirements included? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Rapid voltage changes

|  |  |
| --- | --- |
| Does the power-generating plant comply with the limit value for rapid voltage changes specified in section 4.6.1.3? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. DC content

Please only complete this section for **power park modules**.

|  |  |
| --- | --- |
| Does the DC content during normal operation exceed 0.5% of nominal current, as specified in section 4.6.1.1? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Voltage unbalance

Please only complete this section for **power park modules**.

|  |  |
| --- | --- |
| Does the plant have balanced three-phase load, as specified in section 4.6.1.2? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Flicker

Please only complete this section for **power park modules**.

|  |  |
| --- | --- |
| Is the flicker contribution for the entire plant below the limit value specified in section 4.6.1.4? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Harmonic overtones

Please only complete this section for **power park modules**.

|  |  |
| --- | --- |
| Are all the harmonic overtones for the entire plant below the limit values specified in 4.6.1.5? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Interharmonic overtones

Please only complete this section for **power park modules**.

|  |  |
| --- | --- |
| Are all the interharmonic overtones for the entire plant below the limit values specified in section 4.6.1.6? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Distortions in the 2-9 kHz frequency range

Please only complete this section for **power park modules**.

|  |  |
| --- | --- |
| Are emissions of distortions in the 2-9 kHz frequency range less than 0.2% of In as required in section 4.6.1.7? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + 1. Protection

|  |  |
| --- | --- |
| Is the power-generating plant equipped with the protection functions required in section 4.5.3? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Islanding detection

|  |  |
| --- | --- |
| Is the power-generating plant equipped with the protection functions required in section 4.5.4? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + - 1. Additional requirements for grid protection of synchronous power-generating plants

Please complete this section for **synchronous** power-generating plants.

|  |  |
| --- | --- |
| Is a synchronous undervoltage relay used? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |
| Is an overcurrent relay used?If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + 1. Requirements for information exchange

|  |  |
| --- | --- |
| Is the power-generating plant capable of exchanging information as required in section 4.7? If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + 1. Signature

|  |  |
| --- | --- |
| Date: |  |
| Contractor:  |  |
| Manager:  |  |
| Signature (manager):  |  |
| Plant owner:  |  |
| Signature (plant owner):  |  |

* 1. Documentation for type B power-generating plants (part 2)

Please complete the documentation with *power-generating plant* data after commissioning and send it to the *DSO*.

* + 1. Identification

|  |  |
| --- | --- |
| Power-generating plant name:  |  |
| Global Service Relation Number (GSRN number):  |  |
| Power-generating plant owner name and address:  |  |
| Power-generating plant owner telephone number:  |  |
| Power-generating plant owner email address:  |  |

* + 1. Active power control
			1. Power reponse to overfrequency

|  |  |
| --- | --- |
| Is the frequency response function for overfrequency enabled? If yes, what are the set point values? Frequency threshold (fRO): Droop: Intentional delay for islanding detection:  | Yes [ ] No [ ] \_\_\_\_\_\_\_\_Hz\_\_\_\_\_\_\_\_%\_\_\_\_\_\_\_\_ms |

* + - 1. Absolute power limit function

|  |  |
| --- | --- |
| Is the absolute power limit function enabled? If yes, which set point value is used?  | Yes [ ] No [ ] Controlled online [ ] \_\_\_\_\_\_\_\_kW |

* + - 1. Ramp rate limit

|  |  |
| --- | --- |
| Is the power-generating plant ramp rate limit enabled? If yes, which set point value is used? | Yes [ ] No [ ] Controlled online [ ] \_\_\_\_\_% Pn/min |

* + 1. Reactive power control
			1. Q control

|  |  |
| --- | --- |
| Is the Q control function enabled? If yes, which set point is used? (Values different from 0 kVAr must be agreed with the DSO)  | Yes [ ] No [ ] Controlled online [ ] \_\_\_\_\_\_\_\_kVAr |

* + - 1. Power Factor control

|  |  |
| --- | --- |
| Is the Power Factor control function enabled? If yes, which set point is used? (Values different from cosφ 1.0 must be agreed with the DSO)  | Yes [ ] No [ ] Controlled online [ ] \_\_\_\_\_\_\_\_ cosφInductive [ ] Capacitive [ ]  |

* + - 1. Automatic Power Factor control

|  |  |
| --- | --- |
| Is the automatic Power Factor control function enabled? (Must only be enabled subject to prior agreement with the DSO) If yes, which set points are used? Set point 1 – P/Pn Set point 1 – Power Factor (inductive)Set point 2 – P/Pn Set point 2 – Power Factor (inductive)Set point 3 – P/Pn Set point 3 – Power Factor (inductive) | Yes [ ] No [ ] \_\_\_\_\_\_\_\_%\_\_\_\_\_\_ cosφ\_\_\_\_\_\_\_\_%\_\_\_\_\_\_ cosφ\_\_\_\_\_\_\_\_%\_\_\_\_\_\_ cosφ |

* + 1. Protection
			1. Relay settings

Please state the actual values at the time of commissioning in the table below.

|  |  |  |  |
| --- | --- | --- | --- |
| **Protection function** | **Symbol** | **Setting** | **Trip time** |
| Overvoltage (step 2) | U>> |  | V |  | ms |
| Overvoltage (step 1) | U> |  | V |  | s |
| Undervoltage (step 1) | U< |  | V |  | s |
| Overfrequency | *f>* |  | Hz |  | ms |
| Underfrequency | *f<* |  | Hz |  | ms |
| Frequency change | *df/dt* |  | Hz/s |  | ms |

* + - 1. Islanding detection

|  |  |
| --- | --- |
| Are vector jump relays or active islanding detection used?  | Yes [ ] No [ ]  |

* + - 1. Additional relay settings for synchronous power-generating plants

Please complete this section for **synchronous** power-generating plants.

Please state the actual relay setting values at the time of commissioning in the table below.

|  |  |  |  |
| --- | --- | --- | --- |
| **Protection function** | **Symbol** | **Setting** | **Trip time** |
| Overcurrent | I> |  | A |  | ms |
| Synchronous undervoltage\* |  |  | V |  | ms |

\*If synchronous undervoltage relay is used.

* + 1. Conformance testing

|  |  |
| --- | --- |
| Is a plan for conformance testing available as specified in sections 4.8.2?If yes, please provide reference to documentation:  | Yes [ ] No [ ]  |

* + 1. Signature

|  |  |
| --- | --- |
| Date:  |  |
| Contractor:  |  |
| Manager:  |  |
| Signature (manager):  |  |
| Plant owner:  |  |
| Signature (plant owner):  |  |